## Slide 1: Water Handling Operations
Unit 4C - Foam and Foam Proportioning Equipment
Version: January 2023

## Slide 2: Objectives
Discuss why foam is more effective than plain water when performing wildland fire suppression operations.
Discuss foam safety, including guidelines for handling foam products.
Identify and discuss the advantages and disadvantages of manual foam proportioning methods used when performing wildland fire suppression operations.

## Slide 3: Objectives
Identify various operational components of the FoamPro® 1600/1601 and Waterous Aquis 1.5.
Demonstrate the ability to set up, run, have foam solution pumped to a nozzle person, and shut down a foam proportioner.
Discuss basic maintenance, winterization, and troubleshooting methods for foam systems

## Slide 4: Reasons to use foam
Makes water “wetter” (more effective)
Reduces evaporation/improves absorption
Adheres to surfaces for pre-treating fuels and structures
Improves water conservation and usage, especially during mop-up.
Use as holding feature during ignition operations
Restricts oxygen. Reduces fuel temperature to below ignition point.

## Slide 11
THAT Is the question!
To Mix or Not to Mix....

## Slide 12: Safety Concerns
Skin and eye irritant
Dries out skin, boots, gloves, etc.
Caution when using in sensitive areas and waterways

## Slide 13: Safety equipment

## Slide 15: Foam Proportioners

## Slide 16: Manual Foam Proportioners
Operators manually adjust the device to maintain a constant mix ratio when water flow and pressure changes.
  Cannot maintain constant mix ratio over various flow and pressure rates
  Caution with plumbing configuration to not "foam the tank"

## Slide 17: Foam On/off valve at tank
Notes: On/Off valve to foam tank. Must be opened to flow foam.

## Slide 18: Cascade Foam Flo
Simple and effective.
Uses standard fittings and is unpowered.
Caution: Foam can get into the tank if valving is not correctly installed or if internal check ball malfunctions.

## Slide 19: Batch Mixing

## Slide 20: Suction-Side Proportioners

## Slide 22: Automatic Foam Proportioner
The automatic foam proportioner makes an adjustment on its own to maintain a constant mix ratio when water flow and pressure changes.
Waterous Aquis™ 1.5
FoamPro® 1601

## Slide 23: Foam Proportioner
Proportional and automatic
Works on discharge side of pump
Class A foam only
Requires water flow and electrical current
No restrictions due to hose length or number of nozzles
No loss of pressure or flow
Accurate at all flow ranges
Resupply foam without interruption

## Slide 24: Operating the Foam Proportioner Major Components
Operator control module
Motor driver box/module
Paddlewheel flowmeter
Foam pump and electric motor
Calibrate/Inject valve
Inline strainer

## Slide 25: Foam Proportioner
s

## Slide 26: Operator Control Module Panel Mounted
Operating instructions
On/Off switch
Injection rate control
  Adjustable from 0.1%-1.0%
Low concentrate (“LOW CONC.”) light

## Slide 27: Motor Driver Box/Module Normal Operation
Circuit breaker switch “Up” for normal operation
Simulated flow switch “Down” for normal operation

## Slide 28: Paddlewheel Flowmeter

## Slide 29: Foam Pump and Electric Motor

## Slide 30: Calibrate/Inject Valve

## Slide 31: Purging Air
Enter “Simulated Flow”
  Switch to “Up” position
  Preprogrammed for 100 gpm
Valve to “Cal/Flush”
Turn panel switch “On”
Run pump until concentrate flows from dump line

## Slide 32: Purging Air Continued
Turn control panel to “Off” position
Return valve to “Inject”
Exit “Simulated Flow” by returning switch to “Down” position

## Slide 33: Inline Strainer

## Slide 34: Foam Injection Check Valve and Injection Port

## Slide 35: Maintenance/Calibration
  FoamPro 1601 – grease every 50 hours
Calibrating the system:
  Check flow rates
  Flush system
  Purge air/prime system
Follow manufacturer recommendations for service intervals.
  Waterous Aquis 1.5
    6.1 oz., SAE30, non-detergent
Notes: Steps to Prime the Foam Proportioner
1. Make sure that the motor driver box toggle switches are set correctly. (FoamPro® 1601 only; otherwise, skip to step 2.)
“Simulated Flow” switch is in the “Up” position.
“Circuit Breaker” switch is in the “Up” position.
2. Set the Foam Percentage” switch to “1%.”
3. Place a container to collect the output that will be coming from the foam pump through the outflow foam concentrate line.
4. Turn the “Calibrate/Inject” valve to the “Cal/Flush” position.
5. Turn the “Controller Module” switch to the “On” position
Foam concentrate should start flowing into the container. When it is flowing at a steady rate (about 20 seconds), the foam pump is primed and ready for operation.
6. Turn the “Controller Module” switch to the “Off” position.

## Slide 36: Winterization
Drain tank.
Drain lines.
Clean inline "Y" strainer.
Flush with clean water.
Flush with recreational vehicle antifreeze
When in doubt, follow the manual.

## Slide 37: Troubleshooting
Is there foam?
Is there enough water flowing?
Check valves
Paddlewheels
Correct settings on proportioner/control module
Manufacturer’s manual for workflows/common issues

## Slide 38: Objectives
Discuss why foam is more effective than plain water when performing wildland fire suppression operations.
Discuss foam safety, including guidelines for handling foam products.
Identify and discuss the advantages and disadvantages of manual foam proportioning methods used when performing wildland fire suppression operations.

## Slide 39: Objectives
Identify various operational components of the FoamPro® 1600/1601 and Waterous Aquis 1.5.
Demonstrate the ability to set up, run, have foam solution pumped to a nozzle person, and shut down a foam proportioner.